## Benign Behaviours
Normal operation |  |  | Complex emergency operation (two faults occur simultaneously)
No faults happen |  | Action -- normal | Fault 1 | Fault 2 | Actions combo | Fault 1 | Fault 2 | Actions combo
| 1 physical behaviours | 1 network behaviours | 66Bus1 | 66Bus2 | 11000000 | 22Bus1 | 22Bus2 | 00110000
|  |  | 66Bus1 | TRSF2 |  |  | 1 | 1
Simple emergency operation (one phase-to-phase fault occurs) |  |  | 66Bus2 | TRSF1 |  | 22Bus1 | FDR1 | 00101000
Fault ID | Fault location description | Actions | TRSF1 | TRSF2 |  | 22Bus1 | FDR2 | 00100100
66Bus1 | Among CB1_66kV, CB2_66kV, and Transformer1 | Simple Prot 1 | 66Bus1 | TRSF1 | Simple Prot 1 | 22Bus1 | FDR3 | 00100010
66Bus2 | Among CB2_66kV, CB3_66kV, and Transformer2 | Simple Prot 2 | 66Bus2 | TRSF2 | Simple Prot 2 | 22Bus1 | FDR4 | 00100001
TRSF1 | Between transformer1 and CB_TRSF1 | Simple Prot 1 |  | 6 | 1 | 22Bus2 | FDR1 | 00011000
TRSF2 | Between transformer2 and CB_TRSF2 | Simple Prot 2 | 66Bus1 | 22Bus1 | 10100000 | 22Bus2 | FDR2 | 00010100
22Bus1 | Between CB1_22kV and CB_FDR1 | Simple Prot 3 | TRSF1 | 22Bus1 |  | 22Bus2 | FDR3 | 00010010
22Bus2 | Between CB3_22kV and CB_FDR2 | Simple Prot 4 | 66Bus1 | 22Bus2 | 10010000 | 22Bus2 | FDR4 | 00010001
FDR1 | Between CB_FDR1 and FDR1 load | Simple Prot 5 | TRSF1 | 22Bus2 |  |  | 8 | 8
FDR2 | Between CB_FDR2 and FDR2 load | Simple Prot 6 | 66Bus2 | 22Bus1 | 01100000 | FDR1 | FDR2 | 00001100
FDR3 | Between CB_FDR3 and FDR3 load | Simple Prot 7 | TRSF2 | 22Bus1 |  | FDR1 | FDR3 | 00001010
FDR4 | Between CB_FDR4 and FDR4 load | Simple Prot 8 | 66Bus2 | 22Bus2 | 01010000 | FDR1 | FDR4 | 00001001
| 10 physical behaviours | 8 network behaviours | TRSF2 | 22Bus2 |  | FDR2 | FDR3 | 00000110
|  |  |  | 8 | 4 | FDR2 | FDR4 | 00000101
Simple emergency operation (Breaker failure protection) |  |  | 66Bus1 | FDR1 | 10001000 | FDR3 | FDR4 | 00000011
Fault ID | Fault location description | Actions | TRSF1 | FDR1 |  |  | 6 | 6
22Bus1 | Between CB1_22kV and CB_FDR1 | Simple Prot 3 failed, CB2_22KV and CB_TRSF1 opens | 66Bus1 | FDR2 | 10000100
|  |  | TRSF1 | FDR2
22Bus2 | Between CB3_22kV and CB_FDR2 | Simple Prot 4 failed, CB2_22KV and CB_TRSF2 opens | 66Bus1 | FDR3 | 10000010 | In totoal | 45 | 28
|  |  | TRSF1 | FDR3
FDR1 | Between CB_FDR1 and FDR1 load | Simple Prot 5 failed, CB1_22KV opens | 66Bus1 | FDR4 | 10000001
|  |  | TRSF1 | FDR4
FDR4 | Between CB_FDR4 and FDR4 load | Simple Prot 8 failed, CB3_22KV opens | 66Bus2 | FDR1 | 01001000
|  |  | TRSF2 | FDR1
| 4 physical behaviours | 4 network behaviours | 66Bus2 | FDR2 | 01000100
|  |  | TRSF2 | FDR2
|  |  | 66Bus2 | FDR3 | 01000010
|  |  | TRSF2 | FDR3
|  |  | 66Bus2 | FDR4 | 01000001
|  |  | TRSF2 | FDR4
|  |  |  | 16 | 8

## Normal Action
Normal | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | close | close | close | close | close

## Simple Prot Acts
Simple protection 1 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | open | open | open
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | close | close | close | close | close
Simple protection 2 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | open | open | open
IED_FDR | [6 empty] | close | close | close | close | close | close | close
Simple protection 3 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | open | close | close | close | close | close | close
Simple protection 4 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | open | close | close | close | close
Simple protection 5 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | close | open | close | close | close
Simple protection 6 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | close | close | open | close | close
Simple protection 7 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | close | close | close | open | close
Simple protection 8 | Publish GOOSE APPID 0X8001 |  |  | Publish GOOSE APPID 0X8002 |  |  | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 | CB2_66kV | CB3_66kV | CB_TRSF2 | CB1_22kV | CB2_22kV | CB3_22kV | CB_FDR1 | CB_FDR2 | CB_FDR3 | CB_FDR4
IED_TRSF1 | close | close | close
IED_TRSF2 |  |  |  | close | close | close
IED_FDR | [6 empty] | close | close | close | close | close | close | open

## Complext Prot Acts
A0 | Publish GOOSE APPID 0X8001 |  |  | C0 | Publish GOOSE APPID 0X8003 | E0 | Publish GOOSE APPID 0X8003 | G0 | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 |  | CB1_22kV |  | CB_FDR1 |  | CB_FDR3
IED_TRSF1 | close | close | close | IED_FDR | close | IED_FDR | close | IED_FDR | close
A1 | Publish GOOSE APPID 0X8001 |  |  | C1 | Publish GOOSE APPID 0X8003 | E1 | Publish GOOSE APPID 0X8003 | G1 | Publish GOOSE APPID 0X8003
| CB1_66kV | CB2_66kV | CB_TRSF1 |  | CB1_22kV |  | CB_FDR1 |  | CB_FDR3
IED_TRSF1 | open | open | open | IED_FDR | open | IED_FDR | open | IED_FDR | open
B0 | Publish GOOSE APPID 0X8002 |  |  | D0 | Publish GOOSE APPID 0X8003 | F0 | Publish GOOSE APPID 0X8003 | H0 | Publish GOOSE APPID 0X8003
| CB2_66kV | CB3_66kV | CB_TRSF2 |  | CB3_22kV |  | CB_FDR2 |  | CB_FDR4
IED_TRSF2 | close | close | close | IED_FDR | close | IED_FDR | close | IED_FDR | close
B1 | Publish GOOSE APPID 0X8002 |  |  | D1 | Publish GOOSE APPID 0X8003 | F1 | Publish GOOSE APPID 0X8003 | H1 | Publish GOOSE APPID 0X8003
| CB2_66kV | CB3_66kV | CB_TRSF2 |  | CB3_22kV |  | CB_FDR2 |  | CB_FDR4
IED_TRSF1 | open | open | open | IED_FDR | open | IED_FDR | open | IED_FDR | open